## 0. Overview & Methods
Supplementary Workbook — Water Consumption Impact (WCI) Analysis
Companion to: AI Data Centers and the Water Use Feedback Loop (submitted to Water Research)
1. Purpose of this Workbook
This workbook contains the full input data, equations, intermediate calculations, and sensitivity analyses that support the ten-site Water Consumption Impact (WCI) assessment reported in the main manuscript (Section 6). Every numerical result shown in the paper's figures and tables can be reproduced by opening the corresponding sheet; every formula is live and will re-evaluate if an input is changed. The workbook is self-contained: no external links, no macros, and no hidden sheets.
2. Sheet Index
Sheet | Contents
0. Overview & Methods | This sheet. Workbook purpose, sheet index, equations, variable definitions, data sources, colour legend, and reproducibility notes.
1. Inputs | Raw site inputs (W, r, K, PF, population) for each of the ten data centres with source citations. Yellow cells are editable inputs; everything downstream recalculates automatically.
2. WCI Decomposition | Three-factor decomposition WCI = (W/K) × r × PF for each site, with W/K, r, PF, WCI, and C_avg/K tabulated. Includes a six-tier risk classification (OVERLOAD / SEVERE / HIGH / MODERATE / LOW / MINIMAL).
3. Community Equivalence | Translates consumptive water use C_avg into (i) annual household-equivalents at US average residential consumption (0.4146 ML/hh-yr) and (ii) the facility's share of total community water use.
4. Growth Projections | Two growth scenarios projected year-by-year from 2024 to 2035: HIGH (24% CAGR, Microsoft observed) and MODERATE (13% CAGR, US national aggregate, Shehabi 2024). Reports the year in which each site crosses WCI = 100%.
5. Ranked Summary | All sites ranked by WCI (descending) with the full set of decomposition, community-share, classification, and breach-year results on a single row per site. This sheet is the one-page reference.
6. Chart Data | Tidy data tables feeding the manuscript figures (WCI by site, community share, decomposition stacks, growth curves, policy-lever effects). Each block is a standalone plottable range.
7. Policy Sensitivity | Effect on WCI of three policy levers applied in isolation: SITING (W/K multiplier), TECHNOLOGY (target r), MANAGEMENT (target PF). Identifies the dominant lever for each site.
3. Equations
Eq. (1) Water Consumption Impact | WCI = C_peak / K = (W / K) × r × PF
Eq. (2) Consumption (average day) | C_avg = r × W
Eq. (3) Consumption (peak day) | C_peak = C_avg × PF
Eq. (4) Household equivalence | HH_equiv = (C_avg × 365.25) / H_avg, where H_avg = 0.4146 ML / household / year
Eq. (5) Community share | Share = C_avg / (pop × h_pc), where h_pc = 0.000303 ML / person / day
Eq. (6) Growth projection | WCI(t) = WCI(2024) × (1 + g)^t, t = 0, 1, …, 11
Eq. (7) Policy lever — Siting | WCI_site = (α × W/K) × r × PF, α = 0.75 (default)
Eq. (8) Policy lever — Technology | WCI_tech = (W/K) × min(r, r_target) × PF, r_target = 0.25 (default)
Eq. (9) Policy lever — Management | WCI_mgmt = (W/K) × r × min(PF, PF_target), PF_target = 2.0 (default)
4. Variable Definitions and Units
Symbol | Definition · Units · Notes
W | Total water withdrawal by the facility (ML/d). Converted from operator-reported volume; 1 MGD = 3.78541 ML/d.
C | Consumptive use: water permanently removed from the local supply by evaporation in cooling towers (ML/d).
r | Consumptive ratio, r = C/W. Site-specific for Google sites (from Environmental Report 2025, EY-assured); industry average 0.77 assumed otherwise.
K | Host public water system permitted delivery capacity (ML/d), from state environmental permits and utility annual reports.
PF | Peaking factor: peak-day to average-day consumption ratio. Site-specific where available; 2.5 (warm-climate default) or 4.5 (extreme demand) otherwise.
C_avg | Average-day consumptive water use, C_avg = r × W (ML/d).
C_peak | Peak-day consumptive water use, C_peak = C_avg × PF (ML/d).
PUE | Power Usage Effectiveness = total facility energy / IT energy. Reported for Google facilities (2024).
pop | Population served by the host public water system (persons).
h_pc | Per-capita residential water use = 80 gal/day = 0.000303 ML/person/day (USGS 2015 Circular 1441).
H_avg | Average annual household water consumption = 0.4146 ML/household/year (USGS 2015).
g | Compound annual growth rate of facility water demand (unitless). HIGH scenario: 0.24; MODERATE scenario: 0.13.
5. WCI Risk Classification Thresholds
Tier | Definition and interpretation
OVERLOAD (WCI > 1.0) | Peak-day consumption by the single facility exceeds the entire permitted capacity of the host utility. The community cannot physically serve both the data centre and its residents on the worst day without load shedding or emergency supply.
SEVERE (0.50 < WCI <= 1.0) | More than half of host utility capacity is claimed by one facility on the peak day. Routine stress events will produce shortages for residential and commercial users.
HIGH (0.25 < WCI <= 0.50) | A quarter to a half of utility capacity consumed. Growth headroom essentially eliminated; any further facilities will compound the stress.
MODERATE (0.10 < WCI <= 0.25) | Noticeable but manageable. Current capacity accommodates the facility but monitoring and demand-side management are warranted.
LOW (0.05 < WCI <= 0.10) | Minor contribution to utility load. Standard operational planning suffices.
MINIMAL (WCI <= 0.05) | Negligible impact on utility. Data-centre withdrawal is within normal utility variation.
6. Data Sources
• Google LLC. 2025 Environmental Report. Site-level water withdrawal and consumption for 2024, assured by Ernst & Young, p. 110-111.
• Han, M. et al. 2026. National-scale infrastructure and water demand projections for US data centres. (See §3.1.2 for the Wisconsin peaking factor derivation.)
• Shehabi, A. et al. 2024. 2024 United States Data Center Energy Usage Report. Lawrence Berkeley National Laboratory, LBNL-2001637.
• USGS 2015 Circular 1441. Estimated Use of Water in the United States. Basis for per-capita and household residential water use.
• Wisconsin Public Radio (2025). Water-use filings for Microsoft Mount Pleasant / Racine County hyperscale site.
• Google Botetourt County FAQ. Permit data for the 2 MGD Virginia campus.
• Greater Edwards Aquifer Alliance (GEAA) 2025. Permit and utility data for the xAI Colossus facility, Memphis, TN.
• Project Domino 2025. Data on the Meta Lebanon, Indiana campus.
• Microsoft Corporation. 2024 Environmental Sustainability Report. Fleet-level water withdrawal 2022-2024 basis for the HIGH-growth scenario.
7. Colour Legend
Yellow background | Editable hardcoded input. Change these cells to re-run the whole workbook.
Navy header band | Column or section header.
Light-blue band | Section subheader within a sheet.
Light grey row | Alternating body row, for readability only.
Plain white cell | Formula cell. Value is recomputed from inputs; do not overwrite.
8. Reproducibility Notes
All formulas in the workbook are transparent and auditable. To reproduce any published value, open the relevant sheet and trace the cell back to Sheet 1 (Inputs) through the formula-reference chain. To run a scenario, edit the yellow input cells in Sheet 1; every downstream sheet refreshes automatically. No macros are used. The file contains no external links. Unit conversions use the exact factor 1 MGD = 3.78541 ML/d and 1 Mgal = 3.78541 ML.
Workbook version | v6 (supplementary submission)
Last updated | April 2026
Contact | See corresponding author in main manuscript

## 1. Inputs
Sheet 1 — Site Inputs
Raw water-use and host-utility data for ten US data-centre sites. Yellow cells are editable inputs.
Site | State | Operator | W (ML/yr) | W (MGD) | W (ML/d) | r (C/W) | C_avg (ML/d) | K (MGD) | K (ML/d) | PF | C_peak (ML/d) | Population served | PUE (2024) | Source | Source URL | Notes
Lebanon | IN | Meta |  | 1.27 | 4.8075 | 0.77 | 3.7018 | 4.6 | 17.4129 | 6.3 | 23.321 | 18000 | — | Han et al. 2026; Project Domino 2025 | Lebanon IN — City of Lebanon Project Domino staff report | Meta campus; r assumed at industry average; PF from permit application.
Council Bluffs | IA | Google | 5338.6 |  | 14.6163 | 0.716 | 10.4653 | 30 | 113.5623 | 6.5 | 68.0242 | 63000 | 1.09 | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | Two facilities (PUE 1.11/1.07). W=1,410.3 Mgal; C=1,010.2 Mgal. r=C/W.
Mayes County | OK | Google | 4195.4 |  | 11.4864 | 0.752 | 8.6378 | 10 | 37.8541 | 2.5 | 21.5944 | 41000 | 1.11 | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | W=1,108.3 Mgal; C=833.2 Mgal. PF=2.5 (warm-climate default).
The Dalles | OR | Google | 1745.5 |  | 4.7789 | 0.784 | 3.7467 | 4.5 | 17.0343 | 2.21 | 8.2801 | 16000 | 1.08 | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | Two facilities (PUE 1.10/1.06). W=461.1 Mgal; C=361.4 Mgal. PF from permit.
Douglas County | GA | Google | 1680.7 |  | 4.6015 | 0.826 | 3.8008 | 8 | 30.2833 | 2.5 | 9.5021 | 146000 | 1.09 | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | W=444.1 Mgal (7.4 potable + 436.7 reclaimed); C=366.9 Mgal.
Wisconsin Site | WI | Microsoft |  | 0.023 | 0.087064 | 0.77 | 0.06704 | 2 | 7.5708 | 30 | 2.0112 | 12000 | — | Wisconsin Public Radio 2025; Han et al. 2026 §3.1.2 | WPR — Microsoft Mount Pleasant data centre expansion | Mount Pleasant / Racine County. 8.4 M gal/yr; peak-day ratio >30x average from WPR records; r assumed; PF as adopted in Han 2026.
Botetourt County | VA | Google |  | 2 | 7.5708 | 0.77 | 5.8295 | 28 | 105.9915 | 2.5 | 14.5738 | 34000 | — | Google Botetourt County FAQ | Botetourt County — Google Data Center Water FAQ | Permitted 2 MGD; facility ramping; no PUE reported. r assumed.
Memphis | TN | xAI |  | 1 | 3.7854 | 0.77 | 2.9148 | 258 | 976.6358 | 4.5 | 13.1164 | 630000 | — | GEAA 2025 | Protect Our Aquifer — xAI Supercomputer dossier | xAI Colossus facility. Host utility is Memphis Light, Gas & Water (258 MGD). r and PF assumed.
Midlothian | TX | Google | 836.6 |  | 2.2905 | 0.825 | 1.8897 | 36 | 136.2748 | 2.5 | 4.7241 | 40000 | — | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | W=221.0 Mgal; C=182.3 Mgal. City of Midlothian Water (36 MGD combined: Tayman 12 + Auger 24).
Henderson | NV | Google | 1362.7 |  | 3.7309 | 0.576 | 2.149 | 900 | 3406.869 | 2.5 | 5.3725 | 320000 | 1.09 | Google Environmental Report 2025 (p. 110) | Google 2025 Environmental Report | W=359.9 Mgal; C=207.4 Mgal. Low r reflects discharge reuse. Host is SNWA (900 MGD).
Methodology Notes
Unit conversions |  |  | 1 MGD = 3.78541 ML/d (million gallons per day to megalitres per day). 1 M gal = 3.78541 ML.
Consumptive ratio r |  |  | r = C / W. For Google sites, r is computed directly from site-specific withdrawal and consumption reported in Google Environmental Report 2025 (p. 110-111, EY-assured). For non-Google sites, r = 0.77 is adopted as the industry average for evaporative cooling.
Peaking factor PF |  |  | Ratio of peak-day to average-day consumption. Site-specific where permit or utility records are available; otherwise 2.5 (warm-climate default) or 4.5 (extreme demand).
Host utility capacity K |  |  | Permitted delivery capacity in MGD, converted to ML/d. Sourced from state environmental permits and utility annual reports.
Power Usage Effectiveness PUE |  |  | Total facility energy divided by IT energy. Google reports per-facility PUE (2020-2024); fleet average = 1.09 in 2024. PUE is not publicly disclosed for non-Google operators.

## 2. WCI Decomposition
Sheet 2 — WCI Three-Factor Decomposition
WCI = (W/K) × r × PF = C_peak / K. Risk class thresholds are defined in Sheet 0 §5.
Site | W/K (demand scale) | r (consumptive ratio) | PF (peaking factor) | WCI | WCI (%) | C_avg / K | C_avg/K (%) | Classification | Dominant factor | Interpretation
Lebanon | 0.27609 | 0.77 | 6.3 | 1.3393 | 133.9% | 0.21259 | 21.26% | OVERLOAD | r (technology) | OVERLOAD: peak consumption exceeds entire utility capacity. Extreme peaking factor is the binding constraint.
Council Bluffs | 0.12871 | 0.716 | 6.5 | 0.599 | 59.9% | 0.092154 | 9.215% | SEVERE | r (technology) | SEVERE: peak consumption claims 60% of utility capacity. Large facility footprint amplified by high PF.
Mayes County | 0.30344 | 0.752 | 2.5 | 0.57046 | 57.05% | 0.22819 | 22.82% | SEVERE | r (technology) | SEVERE: 57% of utility consumed. Rural Oklahoma utility; demand scale dominates.
The Dalles | 0.28055 | 0.784 | 2.21 | 0.48609 | 48.61% | 0.21995 | 21.99% | HIGH | r (technology) | HIGH: 49% of utility consumed. Small-city utility with a large facility on demand-scale basis.
Douglas County | 0.15195 | 0.826 | 2.5 | 0.31377 | 31.38% | 0.12551 | 12.55% | HIGH | r (technology) | HIGH: 31% consumed. Large county utility; arid climate drives high r.
Wisconsin Site | 0.0115 | 0.77 | 30 | 0.26565 | 26.57% | 0.008855 | 0.8855% | HIGH | PF (peaking) | HIGH: extreme PF = 30 drives 27% peak load despite very small average withdrawal.
Botetourt County | 0.071429 | 0.77 | 2.5 | 0.1375 | 13.75% | 0.055 | 5.5% | MODERATE | r (technology) | MODERATE: 14%. Permitted 2 MGD against 28 MGD utility.
Memphis | 0.003876 | 0.77 | 4.5 | 0.01343 | 1.343% | 0.0029845 | 0.2984% | MINIMAL | r (technology) | LOW: 1.3%. Massive 258 MGD Memphis utility absorbs the facility load.
Midlothian | 0.016808 | 0.825 | 2.5 | 0.034666 | 3.467% | 0.013866 | 1.387% | MINIMAL | r (technology) | MINIMAL: 3.5%. Midlothian's 36 MGD system comfortably absorbs facility demand, though DC share of community use is notable given the small population.
Henderson | 0.0010951 | 0.576 | 2.5 | 0.0015769 | 0.1577% | 0.00063078 | 0.06308% | MINIMAL | r (technology) | MINIMAL: 0.2%. SNWA's 900 MGD system makes facility contribution negligible.
Risk Classification Thresholds
OVERLOAD | WCI > 1.00 |  |  | Peak-day consumption by the facility exceeds the entire permitted utility capacity.
SEVERE | 0.50 < WCI ≤ 1.00 |  |  | More than half of utility capacity is claimed by the facility on the peak day.
HIGH | 0.25 < WCI ≤ 0.50 |  |  | A quarter to a half of utility capacity consumed; growth headroom eliminated.
MODERATE | 0.10 < WCI ≤ 0.25 |  |  | Noticeable but manageable; demand-side measures warranted.
LOW | 0.05 < WCI ≤ 0.10 |  |  | Minor contribution to utility load; standard operational planning suffices.
MINIMAL | WCI ≤ 0.05 |  |  | Negligible impact on utility; within routine variation.

## 3. Community Equivalence
Sheet 3 — Community Water Equivalence
Translates facility consumption into household-equivalent and community-share terms.
Site | C_avg (ML/d) | C_annual (ML/yr) | Household equivalent | Population served | Per-capita use (ML/d) | Community total (ML/d) | DC / Community (%) | DC equivalent residents | Interpretation
Lebanon | 3.7018 | 1352.0651 | 3261.1314 | 18000 | 0.000303 | 5.454 | 67.87% | 12217.0047 | Facility consumes water equivalent to 68% of the entire small-city community's residential demand.
Council Bluffs | 10.4653 | 3822.4376 | 9219.5794 | 63000 | 0.000303 | 19.089 | 54.82% | 34538.8244 | Equal to 55% of the 63,000-person community's residential water use.
Mayes County | 8.6378 | 3154.9408 | 7609.6015 | 41000 | 0.000303 | 12.423 | 69.53% | 28507.4493 | Equal to 70% of the 41,000-person rural community's residential water use.
The Dalles | 3.7467 | 1368.472 | 3300.7043 | 16000 | 0.000303 | 4.848 | 77.28% | 12365.2546 | Equal to 77% of a 16,000-person town's residential water use.
Douglas County | 3.8008 | 1388.2582 | 3348.4279 | 146000 | 0.000303 | 44.238 | 8.592% | 12544.039 | Equal to 9% of the 146,000-person county's residential water use.
Wisconsin Site | 0.06704 | 24.4862 | 59.0599 | 12000 | 0.000303 | 3.636 | 1.844% | 221.2528 | Equal to 2% of the community's residential water use (tiny facility; dominant stress is peaking).
Botetourt County | 5.8295 | 2129.2363 | 5135.64 | 34000 | 0.000303 | 10.302 | 56.59% | 19239.3776 | Equal to 57% of the 34,000-person county's residential water use.
Memphis | 2.9148 | 1064.6182 | 2567.82 | 630000 | 0.000303 | 190.89 | 1.527% | 9619.6888 | Equal to 1.5% of the 630,000-person city's residential water use.
Midlothian | 1.8897 | 690.195 | 1664.725 | 40000 | 0.000303 | 12.12 | 15.59% | 6236.4717 | Equal to 15.6% of the 40,000-person city's residential water use.
Henderson | 2.149 | 784.9152 | 1893.1867 | 320000 | 0.000303 | 96.96 | 2.216% | 7092.3455 | Equal to 2.2% of the 320,000-person metro area's residential water use.
Constants
Average US household water use |  |  | 0.4146 ML/household/year |  |  | USGS 2015 Circular 1441
Per-capita residential use |  |  | 0.000303 ML/person/day (≈ 80 gal/day) |  |  | USGS 2015 Circular 1441

## 4. Growth Projections
Sheet 4 — Growth Projections to 2035
WCI(t) = WCI(2024) × (1 + g)^t. Two scenarios: HIGH (24% CAGR, Microsoft observed) and MODERATE (13% CAGR, US aggregate, Shehabi 2024).
Scenario Parameters
HIGH scenario CAGR | 24% |  | Microsoft observed water CAGR 2022-2024 (12,076 → 18,564 ML).
MODERATE scenario CAGR | 13% |  | US national data centre water growth 2014-2023 (21.2 → 66 BL), Shehabi 2024.
Panel A — HIGH growth scenario
Site | WCI 2024 (base) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Breach year (WCI > 100%)
Lebanon | 1.3393 | 133.9% | 166.1% | 205.9% | 255.4% | 316.6% | 392.6% | 486.9% | 603.7% | 748.6% | 928.3% | 1151% | 1427% | 2024
Council Bluffs | 0.599 | 59.9% | 74.28% | 92.1% | 114.2% | 141.6% | 175.6% | 217.8% | 270% | 334.8% | 415.2% | 514.8% | 638.4% | 2027
Mayes County | 0.57046 | 57.05% | 70.74% | 87.71% | 108.8% | 134.9% | 167.2% | 207.4% | 257.1% | 318.9% | 395.4% | 490.3% | 607.9% | 2027
The Dalles | 0.48609 | 48.61% | 60.27% | 74.74% | 92.68% | 114.9% | 142.5% | 176.7% | 219.1% | 271.7% | 336.9% | 417.8% | 518% | 2028
Douglas County | 0.31377 | 31.38% | 38.91% | 48.25% | 59.82% | 74.18% | 91.99% | 114.1% | 141.4% | 175.4% | 217.5% | 269.7% | 334.4% | 2030
Wisconsin Site | 0.26565 | 26.57% | 32.94% | 40.85% | 50.65% | 62.81% | 77.88% | 96.57% | 119.7% | 148.5% | 184.1% | 228.3% | 283.1% | 2031
Botetourt County | 0.1375 | 13.75% | 17.05% | 21.14% | 26.22% | 32.51% | 40.31% | 49.98% | 61.98% | 76.86% | 95.3% | 118.2% | 146.5% | 2034
Memphis | 0.01343 | 1.343% | 1.665% | 2.065% | 2.561% | 3.175% | 3.937% | 4.882% | 6.054% | 7.507% | 9.308% | 11.54% | 14.31% | —
Midlothian | 0.034666 | 3.467% | 4.299% | 5.33% | 6.61% | 8.196% | 10.16% | 12.6% | 15.63% | 19.38% | 24.03% | 29.79% | 36.94% | —
Henderson | 0.0015769 | 0.1577% | 0.1955% | 0.2425% | 0.3007% | 0.3728% | 0.4623% | 0.5733% | 0.7108% | 0.8814% | 1.093% | 1.355% | 1.681% | —
Panel B — MODERATE growth scenario
Site | WCI 2024 (base) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | Breach year (WCI > 100%)
Lebanon | 1.3393 | 133.9% | 151.3% | 171% | 193.2% | 218.4% | 246.8% | 278.8% | 315.1% | 356% | 402.3% | 454.6% | 513.7% | 2024
Council Bluffs | 0.599 | 59.9% | 67.69% | 76.49% | 86.43% | 97.67% | 110.4% | 124.7% | 140.9% | 159.2% | 179.9% | 203.3% | 229.8% | 2029
Mayes County | 0.57046 | 57.05% | 64.46% | 72.84% | 82.31% | 93.01% | 105.1% | 118.8% | 134.2% | 151.7% | 171.4% | 193.6% | 218.8% | 2029
The Dalles | 0.48609 | 48.61% | 54.93% | 62.07% | 70.14% | 79.25% | 89.56% | 101.2% | 114.4% | 129.2% | 146% | 165% | 186.5% | 2030
Douglas County | 0.31377 | 31.38% | 35.46% | 40.07% | 45.27% | 51.16% | 57.81% | 65.33% | 73.82% | 83.42% | 94.26% | 106.5% | 120.4% | 2034
Wisconsin Site | 0.26565 | 26.57% | 30.02% | 33.92% | 38.33% | 43.31% | 48.94% | 55.31% | 62.5% | 70.62% | 79.8% | 90.18% | 101.9% | 2035
Botetourt County | 0.1375 | 13.75% | 15.54% | 17.56% | 19.84% | 22.42% | 25.33% | 28.63% | 32.35% | 36.55% | 41.31% | 46.68% | 52.74% | —
Memphis | 0.01343 | 1.343% | 1.518% | 1.715% | 1.938% | 2.19% | 2.474% | 2.796% | 3.16% | 3.57% | 4.034% | 4.559% | 5.152% | —
Midlothian | 0.034666 | 3.467% | 3.917% | 4.427% | 5.002% | 5.652% | 6.387% | 7.217% | 8.156% | 9.216% | 10.41% | 11.77% | 13.3% | —
Henderson | 0.0015769 | 0.1577% | 0.1782% | 0.2014% | 0.2275% | 0.2571% | 0.2905% | 0.3283% | 0.371% | 0.4192% | 0.4737% | 0.5353% | 0.6049% | —

## 5. Ranked Summary
Sheet 5 — Ranked Summary of Ten Sites
Single-row-per-site reference. Rows are positionally ordered by unsorted source; see column I (WCI) to rank descending.
Rank | Site | State | Operator | K (MGD) | W/K | r | PF | WCI | WCI (%) | C_avg/K (%) | Household equivalent | DC / Community (%) | Classification | Yrs to 100% (13% CAGR)
1 | Lebanon | IN | Meta | 4.6 | 0.27609 | 0.77 | 6.3 | 1.3393 | 133.9% | 21.26% | 3261.1314 | 67.87% | OVERLOAD | 0
2 | Council Bluffs | IA | Google | 30 | 0.12871 | 0.716 | 6.5 | 0.599 | 59.9% | 9.215% | 9219.5794 | 54.82% | SEVERE | 5
3 | Mayes County | OK | Google | 10 | 0.30344 | 0.752 | 2.5 | 0.57046 | 57.05% | 22.82% | 7609.6015 | 69.53% | SEVERE | 5
4 | The Dalles | OR | Google | 4.5 | 0.28055 | 0.784 | 2.21 | 0.48609 | 48.61% | 21.99% | 3300.7043 | 77.28% | HIGH | 6
5 | Douglas County | GA | Google | 8 | 0.15195 | 0.826 | 2.5 | 0.31377 | 31.38% | 12.55% | 3348.4279 | 8.592% | HIGH | 10
6 | Wisconsin Site | WI | Microsoft | 2 | 0.0115 | 0.77 | 30 | 0.26565 | 26.57% | 0.8855% | 59.0599 | 1.844% | HIGH | 11
7 | Botetourt County | VA | Google | 28 | 0.071429 | 0.77 | 2.5 | 0.1375 | 13.75% | 5.5% | 5135.64 | 56.59% | MODERATE | —
9 | Memphis | TN | xAI | 258 | 0.003876 | 0.77 | 4.5 | 0.01343 | 1.343% | 0.2984% | 2567.82 | 1.527% | MINIMAL | —
8 | Midlothian | TX | Google | 36 | 0.016808 | 0.825 | 2.5 | 0.034666 | 3.467% | 1.387% | 1664.725 | 15.59% | MINIMAL | —
10 | Henderson | NV | Google | 900 | 0.0010951 | 0.576 | 2.5 | 0.0015769 | 0.1577% | 0.06308% | 1893.1867 | 2.216% | MINIMAL | —

## 6. Chart Data
Sheet 6 — Visualization
Each block is a self-contained plot range referenced from live calculation sheets.
Block A — WCI and C_avg/K by site (Fig. 3)
Site | WCI (%) | C_avg/K (%)
Lebanon | 133.9% | 21.26%
Council Bluffs | 59.9% | 9.215%
Mayes County | 57.05% | 22.82%
The Dalles | 48.61% | 21.99%
Douglas County | 31.38% | 12.55%
Wisconsin Site | 26.57% | 0.8855%
Botetourt County | 13.75% | 5.5%
Memphis | 1.343% | 0.2984%
Midlothian | 3.467% | 1.387%
Henderson | 0.1577% | 0.06308%
Block B — Facility share of community water use (Fig. 3b)
Site | DC / Community (%) | Household equivalent
Lebanon | 67.87% | 3261.1314
Council Bluffs | 54.82% | 9219.5794
Mayes County | 69.53% | 7609.6015
The Dalles | 77.28% | 3300.7043
Douglas County | 8.592% | 3348.4279
Wisconsin Site | 1.844% | 59.0599
Botetourt County | 56.59% | 5135.64
Memphis | 1.527% | 2567.82
Midlothian | 15.59% | 1664.725
Henderson | 2.216% | 1893.1867
Block C — Decomposition factors (Fig. 4)
Site | W/K | r | PF | WCI
Lebanon | 0.27609 | 0.77 | 6.3 | 1.3393
Council Bluffs | 0.12871 | 0.716 | 6.5 | 0.599
Mayes County | 0.30344 | 0.752 | 2.5 | 0.57046
The Dalles | 0.28055 | 0.784 | 2.21 | 0.48609
Douglas County | 0.15195 | 0.826 | 2.5 | 0.31377
Wisconsin Site | 0.0115 | 0.77 | 30 | 0.26565
Botetourt County | 0.071429 | 0.77 | 2.5 | 0.1375
Memphis | 0.003876 | 0.77 | 4.5 | 0.01343
Midlothian | 0.016808 | 0.825 | 2.5 | 0.034666
Henderson | 0.0010951 | 0.576 | 2.5 | 0.0015769
Block D — 13% CAGR trajectories (Figure 5b)
Site | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Lebanon | 133.9% | 151.3% | 171% | 193.2% | 218.4% | 246.8% | 278.8% | 315.1% | 356% | 402.3% | 454.6% | 513.7%
Council Bluffs | 59.9% | 67.69% | 76.49% | 86.43% | 97.67% | 110.4% | 124.7% | 140.9% | 159.2% | 179.9% | 203.3% | 229.8%
Mayes County | 57.05% | 64.46% | 72.84% | 82.31% | 93.01% | 105.1% | 118.8% | 134.2% | 151.7% | 171.4% | 193.6% | 218.8%
The Dalles | 48.61% | 54.93% | 62.07% | 70.14% | 79.25% | 89.56% | 101.2% | 114.4% | 129.2% | 146% | 165% | 186.5%
Douglas County | 31.38% | 35.46% | 40.07% | 45.27% | 51.16% | 57.81% | 65.33% | 73.82% | 83.42% | 94.26% | 106.5% | 120.4%
Wisconsin Site | 26.57% | 30.02% | 33.92% | 38.33% | 43.31% | 48.94% | 55.31% | 62.5% | 70.62% | 79.8% | 90.18% | 101.9%
Botetourt County | 13.75% | 15.54% | 17.56% | 19.84% | 22.42% | 25.33% | 28.63% | 32.35% | 36.55% | 41.31% | 46.68% | 52.74%
Memphis | 1.343% | 1.518% | 1.715% | 1.938% | 2.19% | 2.474% | 2.796% | 3.16% | 3.57% | 4.034% | 4.559% | 5.152%
Midlothian | 3.467% | 3.917% | 4.427% | 5.002% | 5.652% | 6.387% | 7.217% | 8.156% | 9.216% | 10.41% | 11.77% | 13.3%
Henderson | 0.1577% | 0.1782% | 0.2014% | 0.2275% | 0.2571% | 0.2905% | 0.3283% | 0.371% | 0.4192% | 0.4737% | 0.5353% | 0.6049%

## 7. Policy Sensitivity
Sheet 7 — Policy Lever Sensitivity
Effect on WCI of three policy levers applied in isolation. Yellow cells are editable targets.
Lever Targets (edit to re-run) | [14 empty] | Figure 5a — plot data
Siting multiplier α | 0.75 | W/K multiplier (0.75 = move facility to a utility 33% larger for the same W). | [12 empty] | Site | Siting Δ | Technology Δ | Management Δ
Technology target r | 0.25 | Target consumptive ratio (0.25 ≈ closed-loop / dry-cooling hybrid). | [12 empty] | Lebanon | 25% | 67.53% | 68.25%
Management target PF | 2 | Target peaking factor (2.0 = well-managed demand-shifted operation). | [12 empty] | Council Bluffs | 25% | 65.08% | 69.23%
[15 empty] | Mayes County | 25% | 66.76% | 20%
Site | Baseline W/K | Baseline r | Baseline PF | Baseline WCI | Siting new WCI | Siting Δ | Siting Δ % | Tech new WCI | Tech Δ | Tech Δ % | Mgmt new WCI | Mgmt Δ | Mgmt Δ % | Dominant lever | The Dalles | 25% | 68.11% | 9.502%
Lebanon | 0.27609 | 0.77 | 6.3 | 1.3393 | 1.0045 | 0.33482 | 25% | 0.43484 | 0.90446 | 67.53% | 0.42517 | 0.91412 | 68.25% | Management | Douglas County | 25% | 69.73% | 20%
Council Bluffs | 0.12871 | 0.716 | 6.5 | 0.599 | 0.44925 | 0.14975 | 25% | 0.20915 | 0.38985 | 65.08% | 0.18431 | 0.41469 | 69.23% | Management | Wisconsin Site | 25% | 67.53% | 93.33%
Mayes County | 0.30344 | 0.752 | 2.5 | 0.57046 | 0.42785 | 0.14262 | 25% | 0.18965 | 0.38081 | 66.76% | 0.45637 | 0.11409 | 20% | Technology | Botetourt County | 25% | 67.53% | 20%
The Dalles | 0.28055 | 0.784 | 2.21 | 0.48609 | 0.36456 | 0.12152 | 25% | 0.155 | 0.33108 | 68.11% | 0.4399 | 0.046189 | 9.502% | Technology | Memphis | 25% | 67.53% | 55.56%
Douglas County | 0.15195 | 0.826 | 2.5 | 0.31377 | 0.23533 | 0.078444 | 25% | 0.094968 | 0.21881 | 69.73% | 0.25102 | 0.062755 | 20% | Technology | Midlothian | 25% | 69.7% | 20%
Wisconsin Site | 0.0115 | 0.77 | 30 | 0.26565 | 0.19924 | 0.066412 | 25% | 0.08625 | 0.1794 | 67.53% | 0.01771 | 0.24794 | 93.33% | Management | Henderson | 25% | 56.6% | 20%
Botetourt County | 0.071429 | 0.77 | 2.5 | 0.1375 | 0.10313 | 0.034375 | 25% | 0.044643 | 0.092857 | 67.53% | 0.11 | 0.0275 | 20% | Technology
Memphis | 0.003876 | 0.77 | 4.5 | 0.01343 | 0.010073 | 0.0033576 | 25% | 0.0043605 | 0.0090698 | 67.53% | 0.005969 | 0.0074612 | 55.56% | Technology
Midlothian | 0.016808 | 0.825 | 2.5 | 0.034666 | 0.026 | 0.0086665 | 25% | 0.010505 | 0.024161 | 69.7% | 0.027733 | 0.0069332 | 20% | Technology
Henderson | 0.0010951 | 0.576 | 2.5 | 0.0015769 | 0.0011827 | 0.00039424 | 25% | 0.00068444 | 0.00089251 | 56.6% | 0.0012616 | 0.00031539 | 20% | Technology
Interpretation Notes
• Each lever is applied to one factor only, holding the other two at their current values. This isolates the marginal benefit of the lever and is conservative relative to any combined intervention.
• MIN() guards ensure that a site already performing better than the target on a given factor is not penalised (new WCI ≤ baseline by construction).
• The Siting lever is modelled as a W/K multiplier because physical relocation and utility capacity expansion are interchangeable for the purposes of the ratio.
• The dominant lever column indicates which intervention delivers the largest absolute WCI reduction for each site; this is actionable policy guidance derived mechanically from the decomposition.
• For sites already classified MINIMAL or LOW (Memphis, Mesa, Henderson), all levers produce only marginal gains; intervention should be directed elsewhere.